|  | CrystaLite, Inc. 3307 Cedar Street Everett, WA 98201 | 1-800-666-6065 www.CrystaLiteInc.com info@crystaliteinc.com | CSI Specification: |
| --- | --- | --- | --- |
|  |  |  | Series 1100 Smoke and Heat Vent |

07 72 00 – Series 1100 Smoke and Heat Vent

### Job Name:

Description:

- GENERAL

  - SECTION INCLUDES

    - This section covers all work necessary for the execution and completion of product(s) as shown on drawings and specified herein.

    - Work includes but is not limited to the following: design and fabrication of product(s) as required.

  - REFERENCE

    - American Architectural and Manufacturers Association

    - American Standards and Test Methods

    - International Building Code

    - National Fenestration Rating Council

    - Underwriter Laboratories

  - DESIGN REQUIREMENTS

Note: Remove all non-pertinent information. Edit as required.

    - Smoke and Heat Vents shall be designed to meet or exceed the following criteria:

      - International Building Code Sections 910.3 - 910.3.4

      - International Building Codes Section 2610.3

    - Tested in accordance to ASTM C 1363 per NFRC requirements, NFRC 201 procedures, and ASTM E 972 / ASTM E 1084. NFRC COG Values:

      - Clear over Clear

        - U-Factor: 0.60

        - SHGC: 0.52

        - VT: 0.43

      - White over Clear

        - U-Factor: 0.60

        - SHGC: 0.75

        - VT: 0.77

    - Product shall be designed to automatically open when triggered by a UL Listed Fusible Link.

    - Product shall be certified in accordance to UL 793 standard for Automatically Operated Roof Vents for Smoke and Heat.

      - 250 full stroke cycle testing without damage

      - 155 mph (60 psf) wind uplift load - 5 time cycle without damage

      - Operates with additional 184 lb uniform static snow load

      - Undamaged after dynamic 100 lb. drop bag impact from a height of 4 feet.

      - Class 30 and Class 60 roof system rating

  - SUBMITTALS

    - Submit full scale shop drawings indicating methods of construction, location and spacing of anchorage, joinery, finishes, size, shape, thickness of framing members, relationship to adjoining work and glazing materials used.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver materials to site in manufacturer’s original and unopened packaging with parts manifest.

    - Store on site in a location and manner to avoid damage. Stacking should be done in a manner that will prevent damage. Store material in a clean, dry location away from high traffic areas. Any protection on the skylights during transportation should remain until installed.

    - Keep handling on site to a minimum. Exercise caution to avoid damage to finishes of material.

- PRODUCTS

  - MANUFACTURER

    - Drawings and specifications are based on products manufactured by:

      - CrystaLite, Inc.

3307 Cedar Street

Everett, WA 98201

1-800-666-6065

www.crystaliteinc.com

      - Substitutions:  Not permitted.

  - MATERIALS

    - Model A Fusible Link

      - UL Listed in 135, 165, 212, 286, 350, 370, 386 degrees F.

      - Material: Bismuth Alloy

    - Aluminum.

      - Aluminum extruded components shall be alloy 6063-T5, of sufficient thickness for this application, and as required per structural calculations; ASTM B 221.

      - Aluminum sheet and plate shall be alloy 5052-H32 per ASTM B 209.

      - Mill Finish.

    - Outer Dome

      - Co-polyester alloy monolithic sheet, shall meet or exceed the following:

        - Rate of Burn, per ASTM D 635: CC1 classification

        - ICC-ES listings as CC1 approved plastic complying with Section 2606.4 of the IBC

        - ANSI Z97.1 Safety Glazing Requirements

        - Miami-Dade County Product Notice of Acceptance-Plastics

        - Light-transmitting plastic in accordance with Section 2608 of the IBC

        - Weathering data in accordance to ICC-ES AC16

    - Inner Dome

      - Impact Modified Acrylic Plastic, shall meet or exceed the following:

        - ICC-ES listings as CC2 approved plastic complying with Section 2606.4 of the IBC

        - ANSI Z97.1 Safety Glazing Requirements

        - Underwriters Laboratories (UL) listings as UL 94HB and UL746 Compliant

        - Miami-Dade County Product Notice of Acceptance-Plastics

        - ASTM D-4802 B-1 Plastics

  - FASTENERS

    - Exterior fasteners and fasteners exposed to wet areas in frame shall be 300 series stainless steel per ASTM 193/A 193M, except pop rivets used on glazing cap are aluminum or stainless steel per manufacturer.

    - Dry area fasteners shall be cadmium-plated steel per ASTM F 1135 or stainless steel.

    - All welding shall be by the TIG process. All exposed welds to be finished to match frame color where practical.

  - ADHESIVES

    - Glazing tapes per ASTM D 1667, 2240, 3575. All other gaskets, setting blocks, and other materials used in glazing shall be of a type, quality and compatibility to provide performance of the skylight(s) covered in this section.

    - Silicone sealant per CAN/CGSB 19.13-M87; TT-S-001543A/ASTM C 920, Type S, NS, Class 25 use NT, G, A&O test requirements.

  - ACCESSORIES

Note: Remove all non-pertinent information. Edit as required.

    - Elite (cable) OR Defense (bars) Fall Protection Safety Grids

      - Safety grid(s) demonstrate performance which exceeds Occupational Safety and Health Administration (OSHA) and the Washington Industrial Safety and Health Act (WISHA) requirements for providing fall protection; static loads of 200 lbs and 800 lbs respectively. Safety grid(s), resisted without failure dynamic impacts of 800 lbs created by a 200 lbs heavy bag released from 48 inches; followed by holding 1,038 lbs of static load for 5 minutes. Testing was witnessed for verification by a third party accredited testing laboratory. Test report available upon request.

    - Self-flashing Insulated Aluminum Curb

      - Aluminum sheet and plate shall be alloy 5052-H32 per ASTM B 209.

      - Curb shall be insulated with Thermasheath rigid foam plastic thermal insulation board composed of polyisocyanurate foam core bonded to reinforced aluminum foil facers on each side. Thickness shall be 1" nominal providing 5.9 R-Value determined by ASTM C518.

  - FABRICATION

    - Product(s) shall be factory fabricated and preassembled in largest size assemblies possible with considerations for shipping and jobsite handling.

    - Product(s) shall have properly designed weep systems for drainage to exterior.

- EXECUTION

  - INSTALLATION

    - Framing shall be installed and glazed by experienced workmen in accordance with the approved shop drawings, manufacturer’s instructions and glazing standards.

  - CLEANING AND PROTECTION

    - Subsequent to installation of product(s) the General Contractor shall be responsible for the cleanup and protection of all materials provided per this section, including, but not limited to glazing materials and framing members. No abrasive materials of any kind shall be used in cleaning of product surfaces.

  - WARRANTY

    - Smoke vents shall be warranted against manufacturer’s defects for a period of five (5) years from date of purchase.

    - Warranty replacement units will be remanufactured in the same size and description as the original units only and does not include removal of defective unit or installation of replacement unit. Warranty period will remain in effect from the original date of delivery. Warranty orders will be chargeable items with proper credit given upon return and inspection of original item.

    - Any modification and/ or changes to the smoke vent without the written consent will render the warranty null and void.